## BASIC
Topic | Type | Inspection | Task | Priority |  |  |  | Frequency
|  |  |  | I | II | III | D | MO | QTRLY | YRLY
A1010 -Standard Foundation | Cracks & Separation | Check that the observed cracks or separations are no more than hairline if the structure is used and is less than 10 years old. | [7 empty] | Y
| Drainage | Check that the grade slopes away from the foundation at least 1 inch vertically per foot, horizontally for the first 5 feet all around the perimeter (may be less where paving occurs). | If necessary, revise the grade with sandy clay (not sand alone) fill or add underground drainage.
|  | Check that gutters and downspouts are clean and water from downspouts is directed away from the foundation. | [7 empty] | Y
|  | Clean catch basins, storm drain inlets, and other conveyance structures in high pollutant load areas just before the wet season. | Schedule annually in August or September | [5 empty] | Q
| Vegetation | Check that there is no broadleaf tree (oak, ash, maple, alder, poplar, etc.) closer to the foundation than a distance equal to the height of the tree, even if the tree is on an adjacent property. (Does not apply if the soil is known to be predominately non-expansive.) | If long existing trees are closer than nominal, consider trimming back the tree to inhibit root growth or consult an arborist. Keep a close eye on the foundation in these areas. | [6 empty] | Y
|  | Check that there is no conifer tree (e.g., pine) closer to the foundation than a distance equal to the radius of its canopy, even if the tree is on an adjacent property. (Does not apply if the soil is known to be predominately non-expansive.) | If long existing trees are closer than nominal, consider trimming back the tree to inhibit root growth or consult an arborist. Keep a close eye on the foundation in these areas. | [6 empty] | Y
|  | Check for vegetation in front of fresh air intakes. | If found remove vegetation. | [5 empty] | Q
| Water Leaks | Check that swimming pools, ponds, and fountains hold water without leaking. | If losing water, check for leakage on supply and return lines. If no leakage is found in the pond, it may need to be drained to find the leak. | [6 empty] | Y
|  | Check that there are no leaks near the foundation, such as a faucet drip or a condensate drip from an air conditioning unit. | If found, repair as needed. | [5 empty] | Q
A2020 - Walls for subgrade enclosure | A2020 - Walls for subgrade enclosure | Check to see if there is water penetration into the basement. | [5 empty] | M
|  | Check that the grade slopes away from the foundation at least 1 inch vertically per foot, horizontally for the first 5 feet all around the perimeter (may be less where paving occurs). | [7 empty] | Y
A4010 - Standard Slabs on Grade | Slab Integrity | Walk the interior and verify pad is level. Check that there are no uncomfortable floor slopes, easily noticed by walking each room. | If you suspect the slab to be unlevel during a walk through, use a 4' to 6' level or laser level to check for slope. If unlevel, search for the reason why. Re-engineering may be needed.
|  | Look for moisture seeping up through concrete pad: discoloration, blistering of the flooring, swelling and lifting of the flooring. | Check for the source of the moisture and effect repairs.
A4040 - Pits and Bases | Piers and Equipment bases; Pits | Check for water penetration.
Check for settling.
A6010 Water gas mitigation
B1010 - Floor Construction | Dimensional Lumber Joists | Walk the interior and verify that the floor is level.
| Wood Truss | Walk the interior and verify that the floor is level.
| Post & Beam with Decking | Walk the interior and verify that the floor is level.
| Pre-stressed concrete | Look for moisture seeping through concrete.
Look for swelling and lifting of the flooring.
| Metal & Concrete | Look for moisture seeping through concrete.
Look for swelling and lifting of the flooring.
B1020 - Roof Construction | Dimensional Lumber Joists | Check for raised areas indicating detached or swelled sheathing.
| Wood Truss | Check for raised areas indicating detached or swelled sheathing.
| Pre-stressed concrete | Look for moisture seeping through concrete: discoloration, blistering, and rust.
| Metal & Concrete | Look for moisture seeping through concrete: discoloration, blistering, and rust.
B1080 - Stairs | Wood | Check that stairs are not squeaking or sagging.
Check that hand railings are securely fastened.
| Concrete | Check for settling.
Check that hand railings are securely fastened.
| Metal | Check that hand railings are securely fastened.
| Masonry | Check for settling.
Check that hand railings are securely.
B2010 - Exterior Walls | Masonry | Check for efflorescence seeping from walls. | Check for areas where water might be entering into the masonry and seal any areas found. Clean efflorescence areas and re-seal or re-paint.
|  | Watch for vandalism. | Keep a record of the last anti-graffiti application if used. Make sure that it is kept up to date. Remove any vandalism as soon as possible after it occurs (one hour response time recommended).
| Siding | Check painted surfaces for paint failure, peeling, chipping, blistering, chalking, water damage, or mildew. | Thoroughly clean and prepare affected areas, and repaint with anti-mildew additive if necessary.
| Trawled on Surfacing | Check surfaces for material failure; peeling, chipping, blistering, chalking, panel warping or separation from structure. | Determine the reason for structure failure and make subsurface repairs. Repair the surface with the appropriate materials.
B2020 - Exterior Windows | Window Integrity | Check the windows for cracked or broken glass. | Repair broken panes.
Check for holes in screens.
B2050 - Exterior Doors and Grilles | Door Integrity | Examine all door lock hardware to make sure it functions easily. | Lubricate keyways and latch sets annually.
|  | Check door closers for proper operation and hydraulic fluid leaks. | Replace badly leaking closers. Adjust swing speed, back check, and latch rate annually.
B2070 - Exterior Louvers and Vents | Louvers | Check to insure that louvers are securely fastened.
| Vents | Check to insure that vents are securely fastened.
B3010 - Roofing | Inspection | Fall restraint systems, inspected annually, and use during inspections. | Install new system if none is present.
|  | Roofing shall be inspected bi-annually (spring and fall). | Create a spreadsheet and establish specific dates for the inspections (for example, third week or September).
|  | Inspect for ponding of water on flat roof areas. | Make repairs to the roof that will allow the water to run to gutters, drains, or scuppers to prevent future deterioration of roof surfaces and possible problems with indoor air quality.
|  | Check gutters, drains and downspouts for debris and leaking joints. | Remove debris and reseal cracked joints.
Flat Roof/Membrane
| Composite Shingle | Check for roof warping. | Check from the attic, where accessible, to see if there are broken or rotted rafters or if the sheathing has pulled away from the rafter. Make repairs as needed. Replace failed sheathing as necessary.
| Metal | Check for deterioration or corrosion of horizontal panel seams, vertical panel seams, panel fasteners and perimeter and penetration flashings.
B3020 - Roof Appurtenances | Antennas | Check to ensure that poles have not slipped down to penetrate roof covering.
Check guy wire stays to make sure they are not pulling out of the roof and causing damage.
| Cupolas | Check for buildup of debris around base.
| Signs | Check to ensure that sign supports are not penetrating roof covering.
Check guy wire stays to make sure they are not pulling out of the roof and causing damage.
| HVAC units | Check that condensate drains are not damaging roof coverings and are properly draining.
Check for buildup of debris around unit.
B3060 - Horizontal Openings/Penetrations | Exhaust fans | Check for buildup of debris around unit.
Chimneys and flues
Ducts
Vent Pipes
| Drains | Check gutters, drains and downspouts for debris and leaking joints. | Remove debris and reseal cracked joints.
| Skylights | Inspect for broken panes and dislodged flashing.
B3080 - Overhead Exterior Enclosures | Awnings | Check for loose connections.
Check for accumulated debris.
| Covered waiting areas | Inspect roof coverings for penetrations.
Check for accumulated debris.
| Gazebos | Inspect gazebo roofs for penetrations.
Check for accumulated debris.
C1010 - Interior Partitions | GWB on wood or metal studs | Inspect for damaged GWB.
Check for nails popping.
Check for signs of moisture or mold.
GWB on metal studs
Masonry
CMU
Operable walls
C1020 - Interior Windows | Door lights
Visibility
C1030 - Interior Doors | Wood
Metal
Roll up
Partitions (accordion, restroom)
| Lock hardware | Check that handles move freely and that the keyways work easily.
| Door closers | Check for leaking oil.
C1040 - Interior Grilles and Grates | Grills & Grates | Check to insure that grills are securely fastened and free of damage or accumulated debris.
Check grates to make sure they are intact and secured.
C1060 - Raised floor construction | Access Flooring | Check that there are no uncomfortable floor slopes.
| Platform/stage floors | Check that there are no uncomfortable floor slopes.
C1070 - Suspended Ceiling Const. | C1070 - Suspended Ceiling Const. | Check that there are no sags in the ceiling.
Check for stained ceiling tile indicating leaks.
C2010 - Wall Finishes | Brick or Masonry | Check for sheer cracks. | Cracks or chipped masonry may be difficult to repair. Mortar can be re-pointed. If the wall is severely out of plumb or cracked replacement should be explored.
Check for chipping or flaking paint
Check for water penetration.
| GWB and Paint | Check for sheer cracks. | Repair as needed and repaint.
Check for holes.
Check for water penetration.
| GWB with Coverings | Check for sheer cracks. | Vinyl covering will need to be repaired or replaced depending upon the severity of the damage.
Check for holes.
Check for water penetration.
| CAB | Check and report any damage immediately. | CAB should be removed from circulation spaces if possible. It can be managed in place but care must be taken whenever work is done around CAB and damaged CAB should be treated as a hazmat incident.
Check for settling or separations.
Check for water penetration.
Check for bulging or out of plumb.
| Wainscotting | Check for separation from GWB. | Repair as needed and repaint.
Check for water penetration.
| Chair Rails | Check for separation from GWB. | Repair as needed and repaint.
C2020 - Interior Fabrications | Plaster wall systems | Check for water penetration.
| Wood cornice, base & window trim | Check for water damage and mold.
C2030 - Flooring | Slab Flooring | Walk the interior and verify pad is level. | If you suspect it to be out of level during walk through, use a 4'to 6' level, or laser level to check for slope. If out of level search for reason why. Re-engineering may be needed.
|  | Look for moisture seeping up through the concrete pad. | Check for the source of the moisture and effect repairs.
| Carpet | Check for wear, stains, fraying, delamination and/or odors. | For wear areas see if it is possible to change the traffic pattern. Effect repairs to carpet as soon as they are discovered as this will keep them from expanding.
| Vinyl | Verify there aer no seam separations, bucklings, cuts, gouges or indentations. | This could be an installation warranty item. Check warranty. Make repairs as soon as possible to prevent the spread of the damage.
| Laminate | Look for buckling, cupping, seam swelling or gaps.
| VCT & Vinyl Tile | Inspect for gaps, buckling and discoloration. | See maintenance action suggestions for vinyl and laminate.
| Ceramic & Porcelain Tile | Check for chipping, splitting, crazing, porosity, cracked grout and porous surface. | Clear loose pieces from affected areas and reinstall with the appropriate adhesives and then re-grout. Apply silicone grout sealer to dried grout. Remove any silicone residue from tile surfaces.
| Gym Floors - Wood | Look for scratches and other damage to surface. | Do not allow the use of chairs, tables or other equipment on the floor without a protective covering for the floor.
C2040 - Stair Finishes | Paints and epoxies | Check for areas of excessive wear.
| Concrete | Check for excessive cracking or chipping.
| Rubber | Check to insure that treads and risers are securely adhered.
Metal
C2050 - Ceiling Finishes | Open | Check for water stains, and peeling paint. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to determine the cause and then effect repairs.
| Painted GWB | Check for water stains. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to determine the cause and then effect repairs.
| Tile | Check for water stains. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to determine the cause and then effect repairs.
| Suspended | Check for water stains, discoloration around light fixtures, soft spots, sages, and peeling paint. | Discoloration in ceilings may be caused from a variety of problems including roof leaks, plumbing leaks and fixtures that are getting too hot. Investigate to determine the cause and then effect repairs.
D1010 - Vertical Conveying Systems | Elevator | Check to see that annual L&I inspections have been done.
| Dumb waiter | Check to see that annual L&I inspections have been done.
| Wheelchair lift | Check to see that annual L&I inspections have been done.
D2010 - Domestic Water Distribution | Supply | Check fixtures for bluish or rust colored stains.
|  | Check circulation pump lubrication and couplers. | Lubricate pumps.
|  | Check backflow prevention valves certification is current. | If out of certification, schedule for re-certification.
|  | Make sure that main water shutoffs are properly marked and documented. | Apply valve tags and purpose if missing.
|  | Check that hot water setpoint is properly adjusted. | Adjust setpoint to no more than 120°F.
D2020 - Sanitary Drainage | Waste | Check roof vents annually to see that they are not plugged or broken off. | Repair or replace.
|  | Check to see that they are not close to intake fans. | Extend pipe up to at least 36 inches above intake or offset 10 feet away and rise up.
D2030 - Building Support Plumbing Systems | Sewer | Check septic system annually or as required by local jurisdictions and document when tanks are pumped. | Schedule the septic tank service if full.
Irrigation
| Fire loop | Check that annual testing is done.
Bio mass loops
D2050 - General Services Compressed Air | Fire sprinkler system (exterior) | Test and blow out condensate on compressor on a monthly basis (or as required).
Check compressor oil levels.
| Pneumatic controls | Test and blow out condensate on compressor on a monthly basis (or as required).
Check compressor oil levels.
| Vocational Ed systems | Test and blow out condensate on compressor on a monthly basis (or as required).
Check compressor oil levels.
Check safety equipment
D3010 - Facility Fuel Systems | Natural Gas | Always keep alert for gas smells.
| Propane | Always keep alert for gas smells.
| Oil | Check fuel filters on a regular basis
D3020 - Heating Systems | Steam | Inspect to insure all equipment is operating and that safety systems are in place. | Pay particular attention to high limit cut offs and water make up switches.
Check water levels.
|  | Verify that the bottom, surface and water column blow downs are occurring and are effective. | Blowing down the boilers regularly helps prevent the buildup of residue which decreases efficiency.
Check and clean/replace filters and strainers on a scheduled basis.
|  | Confirm water treatment is functioning properly. | Sample water weekly.
Change air filters on a regular basis.
| Hot Water | Visually inspect to insure all equipment is operating and that safety systems are in place. | Pay particular attention to high limit cut offs and water make up switches.
Check water levels.
|  | Verify the bottom, surface and water column blow downs are occurring and are effective. | Blowing down the boilers regularly helps prevent the buildup of residue which decreases efficiency.
|  | Confirm water treatment system is functioning properly. | Sample water weekly.
Change air filters on a regular basis.
| Heat Pumps | Change air filters on a regular basis.
| Electric | Check that fans are operating properly.
Change air filters on a regular basis.
Bio Mass
D3030 - Cooling Systems | Heat Pump | Proper refrigerant charge. | Check gages or color indicators that the charge is adequate. The O&M Manual should have this information. Add proper refrigerant if low. Caution: A skilled technician should do this for refrigeration.
Bio Mass
| Chillers | Proper refrigerant charge. | Check gages or color indicators that the charge is adequate. The O&M Manual should have this information. Add proper refrigerant if low. Caution: A skilled technician should do this for refrigeration.
|  | Check that sensors are calibrated and control setpoints are properly adjusted, (found in controls submittal or Systems manual). | Measure medium with calibrated instrument at location of sensor. Calibrate or replace if reading is incorrect. Caution: A skilled technician should do this for refrigeration.
|  | Check equipment operating schedules are appropriate (operates during occupied schedules, off, setback in un-occupied schedule). | Adjust operating times to match occupancy schedule.
| Cooling Towers | Service system biannually. | Recommended, spring and fall.
|  | Inspect equipment and repair as needed. | Lubricate motors and bearings as needed; Adjust drive belts and pulleys as necessary; Remove debris from fan blades and check for damage; Adjust make-up water system as necessary.
Clean air intake screens and sump strainers.
Water treatments shall be performed by trained personnel only.
Verify all chemicals are stored away from all student occupied areas.
D3050 - Facility HVAC Dist. System | Duct
Plenums
Piping
Valves
D3060 - Ventilation | Fans | Check that bearings are properly lubricated. | Apply appropriate lubrication.
|  | Check belts for wear and that they are adjusted properly. | Replace belts and adjust sheaves.
Ducts
| Natural | Check that the occupant understands how the natural ventilation functions. | Train the occupant how to operate the system.
D4010 - Fires Suppression | Extinguishing systems | Check that extinguishing systems are tested and serviced annually.
| Kitchen Hoods | Check that hoods are tested and serviced annually.
| Sprinklers | Check that sprinklers are tested and serviced annually.
D4030 Fire Suppression Specialties |  | Check that extinguishers are tested and serviced annually.
D5010 - Facility Power Generation | Generator | Set up schedule to check oil levels and fuel supply.
Set up test run schedule.
D5020 - Electrical Service and Distribution | Transformers | Check that transformers are secured from the public and that vegetation is removed from around them.
| Vaults | Check that electrical vaults are secured from the public.
Check that worker access is safe.
| Main Subpanels | Check that there is a minimum of 3 feet of clearance in front of all sub-panels.
Check that sub-panels are secured from the public.
EMT, wiring
| Motors | Check lubricant levels on a regular basis
D5030 - General Purpose Electrical Power | Sub-panel to Branch panel wiring; branch panels
D5040 - Lighting | Tubes | Check for lights that are flickering.
Ballasts
| Lens | Check to see that there is no water in the lenses.
| CFC | Check for lights that are flickering.
Switches
Incandescent
HPS, MV, etc.
| Occupancy Sensors |  | Adjust sensitivity of the sensor. Replace if failed.
D5080 - Miscellaneous Electrical Systems | Elevators | Check to see that annual L&I inspections have been done.
Signs
| Pool Systems | Check to insure that pool systems are properly grounded.
| Fuel Dispensing Facilities (bus maintenance Facilities) | Check to insure that fuel islands are properly grounded.
| Bus Garage | See D5020, D5030 and D5040
D6010 - Data Communications | Internet
Wireless connections
| Servers | Check to insure that room AC is working properly.
D6020 - Voice Communications | Land Lines
Radio Systems
D6030 - Audio-Video - Communication | Cable
Satellite
D6060 - Distributed Comm/Monitoring
D7010 - Access Control and Intrusion Defection | Keypads | Check that key cards have not been vandalized
| Electronic Locks | Check system for function, reliability, and speed.
D7030 - Electronic Surveillance | Cameras | Check that cameras have not been vandalized.
| Motion Sensors | Check that motion sensors have not been vandalized.
DVR's
D7050 - Detection and Alarm | Smoke Detectors | Insure that annual testing has occurred, use canned smoke.
| Heat Detectors | Insure that annual testing has occurred.
| Strobes & Horns | Insure that annual testing has occurred.
D8010 - Integrated Automation Facility Controls | DDC
E1010 - Vehicle and Pedestrian Equipment | Hydraulic Lifts | Check to see that annual L&I inspections have been done.
E1030 - Commercial Equipment | Laundry | Check dryer vents for lint buildup.
E1040 - Institutional Equipment | Library
Theatre & Stage
Laboratory
E1070 - Entertainment and Recreational Equipment | LCD Projectors (Installed)
Screens
TV's
E1090 - Other Equipment | Dishwashers (kitchen)
Walk in freezer
Walk in refrigerator
Ovens
Deep fryers
Mixers
E2010 - Fixed Furnishings | Window treatments
Fixed grills and mats
| Fixed multiple seats | Check that bleachers are functioning properly.
Fixed casework
E2050 - Movable Furnishings | Library bookshelves
| Cafeteria tables | Check that torsion assist for raising and lowering tables are functioning.
Check that locking systems are working properly.
Kitchen serving tables
Kitchen food warmers